## Instructions
GIZMo DCS intake | GIZMo Kria — K26 SOM / KR260 implementation
Canonical namespace | urn:fnal:gizmo
Endpoint | opc.tcp://<assigned-host>:4840 (final host/IP assigned by Slow Controls)
Contract | Stable string NodeIds; resolve namespace URI at connection time; do not hard-code namespace index.
Access semantics | Control rows are listed first and color-coded. Green Read-Write rows are bounded configuration setpoints; amber Write-Only rows are typed OPC UA Methods. Read-Only measurement/status rows are device readbacks and must not be writable. Notes identify implemented versus commissioning-gated capabilities.
Command policy | All mutations require authenticated role/state authorization, serialization, bounded execution, audit, result/readback, and explicit failure. A method return means accepted/rejected; it does not by itself prove physical completion.
Excluded controls | No arbitrary shell/service command, controller reboot, raw relay/resistor state, FPGA/MMIO/register write, bitstream programming, or power-cycle control is requested by this intake.
Numeric-field convention | Sensor Span = verified software or documented presentation domain; Nominal Value = requested initial value or a clearly identified current observation; Desired Range = initial normal/check band, while any wider writable authorization appears in Notes; alarm columns = Ignition alarm configuration. Desired ranges extrapolated from history are explicitly labelled provisional and do not create alarms. Blank means no supported value has been established and must not be filled from template examples.
Document status | Draft 0.7 requirements intake for joint GIZMo / Slow Controls review
Prepared | 2026-08-13
Companion ICD | DUNE Interface Document: Slow Controls – Ground Impedance Monitor (GIZMo)
Workbook basis | DCS_Intake_Template.xlsx supplied by DUNE Slow Controls; retained only as the requested intake layout.
SC design basis | DUNE-doc 37315 v.1 bridge/OPC UA/Ignition architecture and June 2026 SC infrastructure/status analysis. Ignition reads each GIZMo OPC UA endpoint directly and owns production tags, alarms, trends, audit, and history; no intermediate history service is requested.
Commissioning evidence | Kria values use the retained 2026-07-27..2026-08-03 permanent SQLite replica as observational evidence. Legacy values use 15 direct coherent frames from the connected ZedBoard on 2026-08-12 plus 27 contiguous deployed-adapter cycles on 2026-08-13; target communication was lost before the 100-cycle acceptance run completed. These sources refine nominal/desired fields but do not replace approved alarm or metrology limits.
Column reference
Column | Meaning
Signal / Tag Name | Short machine name for the tag.
Description | Plain-language description of what the signal is.
OPC-UA Node Address | Full OPC-UA NodeId or browse path the DCS will read.
Data Type | OPC-UA data type. Use the dropdown.
Eng Units | Engineering units ONLY (degC, V, A, psia, bar...). Do NOT put units in the value columns.
Signal Source | Direct = read straight from device. Derived = computed.
Scaling / Derivation | Raw->scaling (slope/offset) OR the formula for derived signals. e.g. (v0-v1)/0.001 ; or raw*0.1-40.
Sensor Span Min | Instrument range low (full measurable span). Used for scaling. Numeric only.
Sensor Span Max | Instrument range high (full measurable span). Numeric only.
Nominal Value | Expected value in normal operation. Numeric only (units go in Eng Units).
Desired Range Min | Low end of normal operating band. Numeric only.
Desired Range Max | High end of normal operating band. Numeric only.
Low Interlock (Trip) | Trip/safety action point on the low side. Leave blank if none. Numeric only.
Low-Low | Second-stage low alarm. Blank if none. Numeric only.
Low | First-stage low alarm. Blank if none. Numeric only.
High | First-stage high alarm. Blank if none. Numeric only.
High-High | Second-stage high alarm. Blank if none. Numeric only.
High Interlock (Trip) | Trip/safety action point on the high side. Blank if none. Numeric only.
Alarm Deadband / Hysteresis | How far the value must recover before the alarm clears. Numeric only.
Alarm On-Delay (s) | Seconds the condition must persist before the alarm fires.
Interlock Action | If this signal trips an interlock, what action must occur?
Access | Read-Only = DCS monitors only. Read-Write = DCS can also set it. Write-Only = command only. Use the dropdown.
Historize? | Should the DCS log this to the historian? Yes/No.
Min Historization Rate | Slowest acceptable logging interval for the historian. Enter an interval in ms, or 'On-Change'. Independent of poll rate.
Poll / Scan Rate (ms) | How often the DCS should read this signal from the device, in milliseconds. e.g. 1000. This is the device poll rate, not the log rate.

## Tag List
Subsystem | Signal / Tag Name | Description | OPC-UA Node Address | Data Type | Eng Units | Signal Source | Scaling / Derivation | Sensor Span Min | Sensor Span Max | Nominal Value | Desired Range Min | Desired Range Max | Low Interlock (Trip) | Low-Low | Low | High | High-High | High Interlock (Trip) | Alarm Deadband / Hysteresis | Alarm On-Delay (s) | Interlock Action | DCS Access | Historize? | Min Historization Rate (ms) | Poll / Scan Rate (ms) | Notes
Configuration | ThresholdOhm | Validated writable integer alarm threshold. | nsu=urn:fnal:gizmo;s=GIZMo.Configuration.ThresholdOhm | Integer | Ohm | Direct | None | 0 | 1000000 | 100 | 100 | 100 | [9 empty] | Read-Write | Yes | On-Change | 1000 | IMPLEMENTED MODEL 1.3. OPC UA UInt32 accepts 0..1,000,000 Ohm. The requested initial/normal setpoint is 100 Ohm, matching the package default and sustained historian value; the initial authorized operator range is 1..500 Ohm. Zero is accepted by firmware but excluded from the operator range because it effectively disables the resistance-threshold branch. Enforce site authorization and verify Measurement.ThresholdOhm after the write.
Configuration | AveragesPerCalculation | Validated writable measurement averaging count. | nsu=urn:fnal:gizmo;s=GIZMo.Configuration.AveragesPerCalculation | Integer | N/A | Direct | None | 1 | 1000000 | 100 | 100 | 100 | [9 empty] | Read-Write | Yes | On-Change | 1000 | IMPLEMENTED MODEL 1.3. OPC UA UInt32 and ZMon accept 1..1,000,000 reads; requested initial/normal value and packaged default are 100. Normal-operator write; verify Measurement.AveragesPerCalculation and a fresh Sequence afterwards.
Operation | ClearLatch | Method: clear the persistent alarm latch. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.ClearLatch | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | IMPLEMENTED MODEL 1.3. OPC UA Method: no input; String result. Normal-operator command; clearing a latch shall not suppress an active physical alarm. Audit through the required model-1.4 command-status nodes.
Operation | StartCalibration | Method: start Kria calibration with requested reads per point. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.StartCalibration | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | IMPLEMENTED MODEL 1.3, MAINTENANCE-ONLY. OPC UA Method: UInt32 reads_per_point input in 1..1,000,000; String acceptance result. Enable for SC only after exclusive hardware ownership, progress/result readback, abort, safe restoration, and controlled calibration activation are commissioned. Never automatic.
Operation | CaptureAdc | Method: request a bounded raw ADC diagnostic capture. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.CaptureAdc | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | IMPLEMENTED MODEL 1.3, MAINTENANCE-ONLY. OPC UA Method: no input; String result. Output size, timeout, ownership, and return to normal acquisition shall be bounded and audited.
Operation | NormalizeMagnitude | Method: request one-shot magnitude normalization. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.NormalizeMagnitude | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | IMPLEMENTED MODEL 1.3, MAINTENANCE-ONLY. OPC UA Method: no input; String result. This is not a traceable calibration and shall not be presented as one.
Operation | SetSystemTime | Method: set the Linux clock using an absolute DateTime. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.SetSystemTime | DateTime | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | IMPLEMENTED MODEL 1.3, MAINTENANCE-ONLY. OPC UA Method: absolute DateTime input; String result. Allowed only when the approved time source cannot recover; verify Time.CurrentUtc/Quality afterwards. Does not assert NTP synchronization.
Operation | RestartMeasurementEngine | Method: restart only the Kria measurement engine and resume its configured normal run mode. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.RestartMeasurementEngine | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | REQUIRED MODEL 1.4, MAINTENANCE-ONLY. OPC UA Method: no input; String acceptance result. A narrow local helper exists today, but this canonical method and its role/state gate, timeout, fresh sequence/PID/hash readback, and audit remain to be implemented. This is not a controller reboot.
Operation | AbortCalibration | Method: abort an active calibration and begin restoration of normal measurement state. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.AbortCalibration | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | REQUIRED MODEL 1.4, MAINTENANCE-ONLY. OPC UA Method: no input; String acceptance result. Must be idempotent and must drive Calibration.OperationState and RestorationState; restoration failure remains latched for maintenance.
Operation | RestoreNormalState | Method: command and verify the approved normal measurement/high-impedance calibration state. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.RestoreNormalState | String | N/A | Direct | None | [14 empty] | Write-Only | No |  |  | REQUIRED MODEL 1.4, MAINTENANCE-ONLY RECOVERY. OPC UA Method: no input; String acceptance result. Physical verification is required before Succeeded; raw relay selection is not exposed.
Operation Status | CommandGateState | Mutating-command gate state: Disabled, Ready, Busy, MaintenanceLocked, or FaultLocked. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.CommandGateState | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. Ignition shall disable command widgets unless this state and the authenticated role permit the requested action.
Operation Status | LastCommandId | Opaque identifier assigned to the most recent accepted or rejected mutating request. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandId | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. Correlates the operator request, device execution, and Ignition audit/history event.
Operation Status | LastCommandName | Canonical name of the most recent accepted or rejected mutating request. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandName | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. Includes configuration writes as well as Method calls.
Operation Status | LastCommandParameters | Bounded, sanitized parameter summary for the most recent mutating request. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandParameters | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 AUDIT READBACK. Secrets and arbitrary command text are prohibited.
Operation Status | LastCommandRequester | Authenticated user/service identity associated with the most recent mutating request. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandRequester | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 AUDIT READBACK. Anonymous production writes are prohibited.
Operation Status | LastCommandState | Execution state: Idle, Accepted, Running, Succeeded, Failed, Rejected, or TimedOut. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandState | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. SC shall not infer physical success from method return alone.
Operation Status | LastCommandRequestTime | UTC source time at which the most recent mutating request was received. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandRequestTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK.
Operation Status | LastCommandCompletionTime | UTC source time at which the most recent mutating request reached a terminal state. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandCompletionTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. Non-good while a command is active or before any command has completed.
Operation Status | LastCommandResult | Bounded result or failure reason for the most recent mutating request. | nsu=urn:fnal:gizmo;s=GIZMo.Operations.LastCommandResult | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. Configuration.LastCommandResult remains as the model-1.3 compatibility value.
Calibration | OperationState | Calibration execution state: Idle, Starting, Running, Restoring, Completed, Failed, Aborted, or Unknown. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.OperationState | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK before StartCalibration is enabled for routine SC use.
Calibration | ProgressPercent | Best available completion estimate for the active calibration operation. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.ProgressPercent | Double | % | Direct | None | 0 | 100 | [12 empty] | Read-Only | Yes | 1000 | 1000 | REQUIRED MODEL 1.4 READBACK. Unknown progress shall carry a non-good StatusCode, not a fabricated zero.
Calibration | LastOperationTime | UTC completion/failure/abort time of the most recent calibration operation. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.LastOperationTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK.
Calibration | LastOperationResult | Bounded calibration result, validation summary, or failure reason. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.LastOperationResult | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 READBACK. A completed sweep is not equivalent to an activated calibration.
Calibration | RestorationState | Post-operation normal-state restoration: NotRequired, Commanded, Verified, Failed, or Unknown. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.RestorationState | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000 | REQUIRED MODEL 1.4 SAFETY READBACK. Verified requires approved evidence of the normal high-impedance measurement state; command completion alone is only Commanded.
Identity | Manufacturer | Organization responsible for the GIZMo runtime package and canonical information model. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.Manufacturer | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000 | IMPLEMENTED MODEL 1.3. Published value: Fermi National Accelerator Laboratory.
Identity | ProductName | Instrument product/platform name. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.ProductName | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Identity | ModelNamespaceUri | Canonical OPC UA namespace URI. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.ModelNamespaceUri | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Identity | ModelVersion | Semantic version of the canonical OPC UA information model. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.ModelVersion | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Identity | RuntimeVersion | Installed GIZMo runtime or adapter version. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.RuntimeVersion | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Identity | Hostname | Host running the OPC UA endpoint. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.Hostname | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Identity | BootId | Boot identifier; changes after target or adapter restart as defined by the platform. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.BootId | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 10000
Identity | DeviceId | Stable privacy-preserving device identifier. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.DeviceId | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Identity | ModelPublicationDate | Publication date of the canonical OPC UA information model. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.ModelPublicationDate | DateTime | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000 | IMPLEMENTED MODEL 1.3. The published model date is 2026-07-27 UTC.
Identity | ServerStartTime | Time the OPC UA server process started. | nsu=urn:fnal:gizmo;s=GIZMo.Identity.ServerStartTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Measurement | Sequence | Monotonic completed-measurement sequence. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.Sequence | Long | N/A | Direct | None | [14 empty] | Read-Only | Yes | 1000 | 1000 | OPC UA built-in type UInt64.
Measurement | SampleTime | Source timestamp for the completed measurement. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.SampleTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | 1000 | 1000
Measurement | ResistanceOhm | Equivalent resistive impedance at the stimulus frequency; valid only while ResistanceRange is InRange. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.ResistanceOhm | Double | Ohm | Direct | None | 0 | 500 |  | 100 | 500 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Kria validated presentation range: 0..500 Ohm. For a finite InRange value, the requested normal band begins at the 100-Ohm threshold. Normal open-loop operation is instead ResistanceRange=OutOfRange (HIGH Z) with non-good StatusCode plus NaN/null; it is not a fabricated 500-Ohm measurement. Ignition shall alarm from Alarm.Active rather than independently comparing this value. Existing permanent Kria SQLite replica, 2026-07-27 20:57 UTC through 2026-08-03 19:07 UTC (560,762 fast samples and 56,082 platform samples). The database is commissioning evidence only; Ignition remains the production OPC UA client and historian.
Measurement | ResistanceRange | Interpretation of ResistanceOhm: InRange, OutOfRange, Invalid, or Unknown. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.ResistanceRange | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Measurement | CapacitanceNanofarad | Equivalent capacitive component estimated by the active calibration. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.CapacitanceNanofarad | Double | nF | Direct | None | 0 | [13 empty] | Read-Only | Yes | 1000 | 1000
Measurement | CapacitanceRange | Interpretation of CapacitanceNanofarad. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.CapacitanceRange | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Measurement | ThresholdOhm | Alarm threshold active in the measurement engine. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.ThresholdOhm | Double | Ohm | Direct | None | 0 | 1000000 | 100 | 100 | 100 | [9 empty] | Read-Only | Yes | On-Change | 1000 | Requested initial readback is 100 Ohm. The Kria historian held 100 Ohm throughout the retained run except for one deliberate two-minute commissioning excursion to 2000 Ohm; that excursion is not a desired operating value. Publish the live device readback.
Measurement | StimulusFrequencyHertz | Nominal sine-wave stimulus frequency. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.StimulusFrequencyHertz | Double | Hz | Direct | None |  |  | 1436 | 1436 | 1436 | [9 empty] | Read-Only | Yes | On-Change | 1000 | Kria configured value from GIZMO_STIMULUS_FREQUENCY_HZ and invariant at 1436 Hz throughout the retained historian interval; the legacy workbook replaces this with its measured value.
Measurement | StimulusCurrentRmsAmpere | RMS AC stimulus current delivered to the detector-ground measurement path. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.StimulusCurrentRmsAmpere | Double | A | Direct | None | 0 | [13 empty] | Read-Only | Yes | 1000 | 1000 | REQUIRED MODEL 1.4 MONITOR VALUE from the Slow Controls analysis. Publish only after the monitor-point transfer function, fundamental-frequency bandwidth, RMS conversion, and uncertainty are validated; until then use a non-good StatusCode and NaN/null. Do not substitute the lock-in magnitude or a front-panel monitor voltage.
Measurement | MagnitudeCount | Lock-in magnitude in uncalibrated ADC counts. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.MagnitudeCount | Double | N/A | Direct | None |  |  | 18525 | 18500 | 18600 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-state commissioning envelope extrapolated from the Kria historian (median about 18,519; 1st--99th percentile minute means about 18,511--18,561). The 521-count absolute minimum occurred during intervention. Trend only; no Ignition alarm is requested.
Measurement | PhaseAtanDegrees | Phase calculated using atan. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.PhaseAtanDegrees | Double | deg | Direct | None | -90 | 90 | -0.46 | -0.55 | -0.35 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Mathematical output range of atan(Q/I); I=0 and non-finite cases require non-good quality. Provisional same-state envelope from retained Kria minute means; excursions associated with commissioning/alarm tests are intentionally excluded. Trend only.
Measurement | PhaseAtan2Degrees | Phase calculated using atan2. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.PhaseAtan2Degrees | Double | deg | Direct | None | -180 | 180 | -0.46 | -0.55 | -0.35 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-state envelope from retained Kria minute means; excursions associated with commissioning/alarm tests are intentionally excluded. Trend only; Alarm.Active remains authoritative.
Measurement | PhaseInterpolatedDegrees | Phase used by impedance calibration interpolation. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.PhaseInterpolatedDegrees | Double | deg | Direct | None |  |  | 0.01 | -0.25 | 1.1 | [9 empty] | Read-Only | Yes | 1000 | 1000 | No validated mathematical span is claimed; the current spline output is not clamped. The desired band is a provisional same-state envelope rounded outward from retained Kria minute means, not an alarm threshold.
Measurement | InPhaseCount | Lock-in in-phase component in ADC counts. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.InPhaseCount | Double | N/A | Direct | None |  |  | 18520 | 18500 | 18600 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-state commissioning envelope extrapolated from retained Kria minute means. Trend only; no Ignition alarm is requested.
Measurement | QuadratureCount | Lock-in quadrature component in ADC counts. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.QuadratureCount | Double | N/A | Direct | None |  |  | -149 | -170 | -120 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-state commissioning envelope extrapolated from retained Kria minute means. Trend only; no Ignition alarm is requested.
Measurement | AveragesPerCalculation | Number of acquisitions averaged in each completed calculation. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.AveragesPerCalculation | Integer | N/A | Direct | None | 1 | 1000000 | 100 | 100 | 100 | [9 empty] | Read-Only | Yes | On-Change | 1000 | OPC UA built-in type UInt32. Requested initial readback; the Kria package default is 100.
Measurement | Quality | Human-readable aggregate quality; clients shall use the OPC UA DataValue StatusCode for logic. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.Quality | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Measurement | Diagnostic | Bounded diagnostic text explaining degraded or bad data quality. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.Diagnostic | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Measurement | LegacyRecord | Original comma-delimited ZMon record retained for engineering audit only. | nsu=urn:fnal:gizmo;s=GIZMo.Measurement.LegacyRecord | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 1000 | Compatibility/audit field only; it is not a physical-data or parsing contract.
Alarm | Active | Authoritative composite alarm decision from the measurement engine. | nsu=urn:fnal:gizmo;s=GIZMo.Alarm.Active | Boolean | N/A | Direct | None |  |  | FALSE | [5 empty] | TRUE |  |  |  | 0 | Annunciate the GIZMo ground-impedance alarm in Ignition; no automatic power or protection action is defined by this interface. | Read-Only | Yes | On-Change | 1000 | Alarm on Boolean True with 0-s SC on-delay and no added hysteresis. In the reviewed Kria engine, the device asserts this state when resistance is strictly below the live ThresholdOhm, or when resistance is greater than 8 Ohm and the absolute difference between interpolated phase and atan2 phase exceeds 1.5 degrees. The retained Kria events contain 14 False-to-True and 14 True-to-False transitions, with ResistanceThreshold and PhaseInterpolation reasons, confirming both branches. DCS shall not recompute this composite state.
Alarm | Latched | Persistent GIZMo alarm latch state. | nsu=urn:fnal:gizmo;s=GIZMo.Alarm.Latched | Boolean | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Alarm | Reason | Reason supplied by the measurement engine for the composite alarm. | nsu=urn:fnal:gizmo;s=GIZMo.Alarm.Reason | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Alarm | LatchTime | Timestamp recorded when the persistent alarm latch was set. | nsu=urn:fnal:gizmo;s=GIZMo.Alarm.LatchTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Thermal | ChassisTemperatureCelsius | Chassis temperature. | nsu=urn:fnal:gizmo;s=GIZMo.Thermal.ChassisTemperatureCelsius | Double | °C | Direct | None |  |  | 35.9 | 33 | 38 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-installation commissioning envelope from the retained Kria historian: median 35.87 degC, 1st--99th percentile minute means 33.38--37.51 degC, absolute observed 30.12--38.12 degC. Trend only; no temperature alarm limit has been approved.
Thermal | Cpu1TemperatureCelsius | CPU temperature sensor 1. | nsu=urn:fnal:gizmo;s=GIZMo.Thermal.CPU1TemperatureCelsius | Double | °C | Direct | None |  |  | 37.3 | 34.5 | 39.5 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-installation commissioning envelope from the retained Kria historian: median 37.27 degC, 1st--99th percentile minute means 34.75--39.07 degC. Trend only; no alarm limit has been approved.
Thermal | Cpu2TemperatureCelsius | CPU temperature sensor 2. | nsu=urn:fnal:gizmo;s=GIZMo.Thermal.CPU2TemperatureCelsius | Double | °C | Direct | None |  |  | 38 | 35 | 40 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-installation commissioning envelope from the retained Kria historian: median 37.97 degC, 1st--99th percentile minute means 35.51--39.73 degC. Trend only; no alarm limit has been approved.
Thermal | Cpu3TemperatureCelsius | CPU temperature sensor 3. | nsu=urn:fnal:gizmo;s=GIZMo.Thermal.CPU3TemperatureCelsius | Double | °C | Direct | None |  |  | 35.4 | 32.5 | 37.5 | [9 empty] | Read-Only | Yes | 1000 | 1000 | Provisional same-installation commissioning envelope from the retained Kria historian: median 35.43 degC, 1st--99th percentile minute means 32.99--37.12 degC. Trend only; no alarm limit has been approved.
Time | NtpSynchronized | True only when the operating system confirms NTP synchronization. | nsu=urn:fnal:gizmo;s=GIZMo.Time.NtpSynchronized | Boolean | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Time | UptimeSeconds | Linux uptime. | nsu=urn:fnal:gizmo;s=GIZMo.Time.UptimeSeconds | Double | s | Direct | None | [14 empty] | Read-Only | Yes | 10000 | 1000
OperatingSystem | CpuUtilizationPercent | CPU utilization between samples. | nsu=urn:fnal:gizmo;s=GIZMo.OperatingSystem.CpuUtilizationPercent | Double | % | Direct | None | 0 | 100 | 35.7 | 30 | 45 | [9 empty] | Read-Only | Yes | 10000 | 10000 | Provisional steady-state commissioning envelope from the retained Kria historian: median 35.68%, 1st--99th percentile minute means 34.30--36.66%; short startup/intervention excursions reached 85.47%. Trend only; no utilization alarm is requested.
OperatingSystem | MemoryAvailableBytes | Physical memory available without swapping. | nsu=urn:fnal:gizmo;s=GIZMo.OperatingSystem.MemoryAvailableBytes | Long | byte | Direct | None | 0 |  | 3170000000 | 2500000000 | 3400000000 | [9 empty] | Read-Only | Yes | 10000 | 10000 | OPC UA built-in type UInt64. Provisional commissioning envelope from the retained Kria historian: median 3.171e9 bytes; absolute observed 2.522e9--3.362e9 bytes. Trend only; no memory alarm is requested.
Firmware | RuntimeVersion | Installed gizmo-runtime package version. | nsu=urn:fnal:gizmo;s=GIZMo.Firmware.RuntimeVersion | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Firmware | OverlayState | FPGA overlay state: Running, Degraded, Missing, or unconfirmed. | nsu=urn:fnal:gizmo;s=GIZMo.Firmware.OverlayState | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Firmware | OverlayBitstreamSha256 | SHA-256 digest of the installed FPGA bitstream. | nsu=urn:fnal:gizmo;s=GIZMo.Firmware.OverlayBitstreamSha256 | String | N/A | Direct | None | [14 empty] | Read-Only | No |  | 30000
Calibration | State | Validity state of the installed production calibration tables. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.State | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Calibration | ConfiguredThresholdOhm | Threshold persisted in package-owned state. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.ConfiguredThresholdOhm | Double | Ohm | Direct | None | 0 | 1000000 | 100 | 100 | 100 | [9 empty] | Read-Only | Yes | On-Change | 30000 | Readback of the persisted device setting. Requested initial value is 100 Ohm, matching the package default and sustained historian value.
Calibration | MeasurementsPerCalculation | Averaging count persisted in package-owned state. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.MeasurementsPerCalculation | Integer | N/A | Direct | None | 1 | 1000000 | 100 | 100 | 100 | [9 empty] | Read-Only | Yes | On-Change | 30000 | OPC UA built-in type UInt32. Requested initial readback matches the packaged default of 100.
Calibration | LastCalibrationTime | Newest modification time among production calibration tables. | nsu=urn:fnal:gizmo;s=GIZMo.Calibration.LastCalibrationTime | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Configuration | LastCommandResult | Result of the most recent canonical write or method call. | nsu=urn:fnal:gizmo;s=GIZMo.Configuration.LastCommandResult | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Health | Overall | Aggregate endpoint health: OK, Degraded, Failed, or Starting. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Overall | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Health | LastUpdate | Time aggregate health was last evaluated. | nsu=urn:fnal:gizmo;s=GIZMo.Health.LastUpdate | DateTime | N/A | Direct | None | [14 empty] | Read-Only | Yes | 1000 | 1000
Health | Measurement | Aggregate quality of the measurement subtree. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Measurement | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Health | Thermal | Aggregate quality of the thermal subtree. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Thermal | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Health | Time | Aggregate quality of timekeeping. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Time | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000
Health | OperatingSystem | Aggregate quality of operating-system telemetry. | nsu=urn:fnal:gizmo;s=GIZMo.Health.OperatingSystem | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 10000
Health | Network | Aggregate quality of network monitoring. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Network | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 10000
Health | Storage | Aggregate quality of storage monitoring. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Storage | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Health | Firmware | Aggregate quality of runtime and programmable-logic state. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Firmware | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Health | Services | Aggregate quality of owned services or adapter processes. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Services | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 10000
Health | Calibration | Aggregate quality of calibration metadata. | nsu=urn:fnal:gizmo;s=GIZMo.Health.Calibration | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 30000
Health | SDR | Aggregate quality of SDR acquisition. | nsu=urn:fnal:gizmo;s=GIZMo.Health.SDR | String | N/A | Direct | None | [14 empty] | Read-Only | Yes | On-Change | 1000